## FRA-detail
[6 empty] | UPRN | B95A1
Fire Risk Assessment (FRA)
Regulatory Reform (Fire Safety) Order 2005
| Next review due on *: |  | As FRA program
| Date of FRA: |  | 2019-06-26
| Responsible person (e.g. housing provider): |  |  | Chief Executive, Barnet Homes
| Fire Risk Assessor |  | The Fire Risk Assessment was undertaken by Mr Philip Holmes who has the necessary qualifications, competency and experience in Fire Risk Management that give him the status of “Competent Person” as described in articles 15 and 18 of the ‘Regulatory Reform (Fire Safety) Order 2005', for properties in England & Wales, and the 'Fire Safety (Scotland) Regulations 2006' for those in Scotland. This legislation now supersedes all previous fire legislation for England, Wales & Scotland and forms the ‘Fire Regulations'. He has been trained in all necessary disciplines of fire safety, building design and building behaviour under fire conditions and is considered to be sufficiently practised in the necessary skills to enable him to carry out a practical fire risk assessment.
(include relevant professional memberships and/or qualifications)
Address of premises: | Person managing fire safety for the premises: |  |  | Health & Safety Manager
Marsh Drive 73-96, NW9 7QQ (B95
| Did you consult with any other individual during the FRA? |  |  |  | No
| If yes, provide | Name
Position within company
| Recommended review date: |  | The person managing fire safety should monitor the progress of work undertaken in rectifying the deficiencies reported and should ensure that checks are undertaken at target completion dates. A follow up inspection (taking the form of an interim fire risk assessment review) should be undertaken no more than one month from the time when the reported ‘Priority P0’ deficiencies have been identified and additionally in six months by which time Priority P1 deficiencies should have been actioned. It is Barnet Homes policy that a review of the fire risk assessment will be undertaken no later than 12 months from the date of inspection.
Euro Compliance Limited
Company Registration: 06353434
Registered office: 90 Milton Avenue, Barnet, Herts, EN5 2EU
Members of the Institute of Fire Engineers
Yes
No

## Premises summary
[6 empty] | UPRN | B95A1
Premises: | Marsh Drive 73-96, NW9 7QQ (B95 |  |  | FRA undertaken on (date): | 2019-06-26
Risk rating | Moderate | Risk rating legend | [5 empty] | Trivial
| The works listed in this report (Action Plan) are recommended to reduce the level of risk to (or maintain it at) Tolerable | [6 empty] | Tolerable
Moderate
Extent of common areas | [7 empty] | Substantial
Internal and external communal areas including the following: entrances, exits, escape stairs, landings, lobbies, electrical intake/service cupboards, refuse areas. Ventilation - open balcony and open ramp. | [7 empty] | Intolerable
Details of building construction (approx. age, structure, cladding, walls, roof)
Concrete framed with brick walls and pitched roof. This block has external cladding. |  | Low | Unusually low likelihood of fire as a result of negligible potential sources of ignition.
|  | Medium | Normal fire hazards (e.g. potential ignition sources) for this type of occupancy, with fire hazards generally subject to appropriate controls (other than minor shortcomings).
|  | High | Lack of adequate controls applied to one or more significant fire hazards, such as to result in significant increases in likelihood of fire.
|  | Slight harm | Outbreak of fire unlikely to result in serious injury or death of any occupant (other than an occupant sleeping in a room in which a fire occurs).
Details of building layout (number of flats, floors, staircases, lifts, etc.) |  | Moderate harm | Outbreak of fire could foreseeably result in injury (including serious injury) of one or more occupants, but it is unlikely to involve multiple fatalities.
24 flats, 6 floors, 2 staircases and 1 lift.
|  | Extreme harm | Significant potential for serious injury or death of one or more occupants.
|  | Risk level | Action and timescale
|  | Trivial | No action is required and no detailed records need be kept.
|  | Tolerable | No major additional controls required. However, there might be a need for improvements that involve minor or limited cost.
How are occupants who warrant special consideration identified? |  | Moderate | It is essential that efforts are made to reduce the risk. Risk reduction measures should be implemented within a defined time period. Where moderate risk is associated with consequences that constitute extreme harm, further assessment might be required to establish more precisely the likelihood of harm as a basis for determining the priority for improved control measures.
In the event of an emergency vulnerability is obtained from the OHMS database available to the Barnet Homes Emergency Officer
|  | Substantial | Considerable resources might have to be allocated to reduce the risk. If the building is unoccupied it should not be occupied until the risk has been reduced. If the building is occupied, urgent action should be taken.
Any other relevant information (including previous fire loss experience)
Barnet Homes Fire Policy and Procedure document forms part of the organisations' Health & Safety Policy and is reviewed by the Board on an annual basis.
|  | Intolerable | Building (or relevant areas) should not be occupied until the risk is reduced.
Areas where access was not available
Inside residents flats.

## FRA
Priority | Description | Timescale |  |  | Over-All Block Risk Rating | UPRN | B95A1
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days |  |  | Any |  |  | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note - RESPONSIVE REPAIRS TEAM | Within 6 months |  |  | Any |  |  | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year |  |  | Substantial |  |  | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years |  |  | Moderate |  |  | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years |  |  | Tolerable |  |  |  | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural |  |  | Ongoing |  |  |  | FRA Team
FIRE RISK ASSESSMENT
NOTE: Please note that whilst we state "recommendations" for the significant findings in this Fire Risk Assessment (Location and comment), these recommendations are the minimum requirements for the 'Responsible Person' in order to comply with the law, in this case the Regulatory Reform Fire Safety Order 2005. They are stated as our 'recommendations' because alternatives may be considered by the responsible person.
Premises: | Marsh Drive 73-96, NW9 7QQ (B95 |  |  | FRA date: | 2019-06-26
Question | Fire safety measures | Yes/No n/k - n/a | Priority | Location and comment
Hazard identification - housekeeping | [6 empty] | 0
1 | Are combustibles separated from ignition sources? | Yes |  |  |  |  | 0
1 | [6 empty] | 0
2 | Is unnecessary storage of combustible materials/waste avoided? | Yes |  | None noted at the time of survey. |  |  | 0
2 | [6 empty] | 0
3 | Are hazardous materials stored appropriately? | n/a |  |  |  |  | 0
Hazard identification - arson | [6 empty] | 0
4 | Are premises secure against arson by outsiders? | No | P1+ | Although there is a secure entry system fitted to this block, the Main Entrance Doors and Landing Entrance Door lockes are broken. These should be repaired/replaced. |  |  | 1
4 | [6 empty] | 1
5 | Are bins secured and stored in a suitable location? | No | P1 | Refuse bins are too close to the means of escape and need to be relocated in a secure area away from the building. |  |  | 2
5 | [6 empty] | 2
6 | Is fire load close to the premises minimised? | Yes |  | No evidence of fire loads near premises. |  |  | 2
6 | [6 empty] | 2
Hazard identification - smoking | [6 empty] | 2
7 | Smoking in inappropriate places. | No |  |  |  |  | 2
7 | [6 empty] | 2
Hazard identification - any other issues - specify | [6 empty] | 2
8 | Is loft hatch secured | Yes |  | Loft hatch is secured with FB14. |  |  | 2
8 | [6 empty] | 2
Means of escape | [6 empty] | 2
9 | Is escape route design satisfactory? (see Home Office guides) | Yes |  | The escape stair is satisfactory for the number of persons expected in the building at any given time |  |  | 2
9 | [6 empty] | 2
10 | Are escape routes clear and unobstructed? | Yes |  |  |  |  | 2
10 | [6 empty] | 2
11 | Is number and provision of exits adequate? | Yes |  | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. |  |  | 2
11 | [6 empty] | 2
12 | Are doors on escape routes easily opened? | Yes |  |  |  |  | 2
12 | [6 empty] | 2
13 | Are travel distances satisfactory - single and two-way? | Yes |  | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. |  |  | 2
13 | [6 empty] | 2
14 | Are escape routes adequately protected? Consider: storage and electrical cupboards, refuse chutes, fire doors (incl. provision, location, self-closers, strips and seals, condition), stair ventilation | No | P3 | There are holes in the ceiling of the electrical intake cupboard and these should be fire stopped by a third party accredited company. |  |  | 3
14 |  | No |  |  |  |  | 3
14 | [6 empty] | 3
14 | [6 empty] | 3
14 | [6 empty] | 3
14 |  | No | P3 | Flat 74 is not an FD30S door and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. |  |  | 4
14 | [6 empty] | 4
14 |  | No | P3 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. |  |  | 5
14 |  | No | P3 | All Flat Entry Doors are not FD30S doors and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. |  |  | 6
14 | [6 empty] | 6
15 | Are escape routes separated (where appropriate)? | n/a |  |  |  |  | 6
15 | [6 empty] | 6
16 | Do escape routes lead to a place of safety? | No | P3 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. |  |  | 7
16 | [6 empty] | 7
17 | Are corridors sub-divided (where appropriate)? | n/a |  |  |  |  | 7
17 | [6 empty] | 7
18 | Are floors free from slipping/tripping hazards? | Yes |  |  |  |  | 7
18 | [6 empty] | 7
19 | Is it considered that the building is provided with reasonable arrangements for means of escape of disabled people? | No | P3 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of +30) particularly as this staircase is the main means of escape in the event of fire. |  |  | 8
19 | [6 empty] | 8
Emergency escape lighting | [6 empty] | 8
20 | Is emergency escape lighting coverage sufficient (internal and external)? | No | P3 | In the event of a fire high level lighting is obscured to the point of no longer being visible thus leaving the area below the smoke layer in darkness (refer to Clause 6.4 of BS5266-1). Therefore, a suitable escape route lighting system should be fitted at low level to ensure that occupants can see for their means of escape in accordance with Article 14(2)(h) the RRFSO which requires an escape route to be provided with illumination of an adequate intensity. The system should be either powered or photoluminescent and fitted to and BS ISO16069:2017 Clause 6 for electrically powered and Clause 7 for photoluminescent systems. Refer to CIBSE Guide E Fire Safety Engineering Guide paragraph 7.8.4. which states systems can be "powered or photoluminescent." |  |  | 9
20 | [6 empty] | 9
21 | Is emergency escape lighting in good working order? | Yes |  | The emergency lights appear to be in good order, last test date 25/04/19. |  |  | 9
21 | [6 empty] | 9
Signage | [6 empty] | 9
22 | Is there adequate provision of fire safety signs and notices? | No | P1 | No Fire Action Notice is displayed. Display Fire Action Notices in prominent positions throughout the premises. |  |  | 10
22 | [6 empty] | 10
22 | [6 empty] | 10
22 | [6 empty] | 10
22 | [6 empty] | 10
22 | [6 empty] | 10
23 | Are signs clearly visible and not obstructed? | Yes |  | Where fitted. |  |  | 10
23 | [6 empty] | 10
Fire detection and alarm | [6 empty] | 10
24 | Is automatic detection and/or manual alarm provided in the premises? If yes, describe system. | n/k | P3 | In accordance with Article 13 of the RRFSO it is deemed that adequate protection is provided if the flats have an LD2 system (this would include all bedrooms), therefore recommend LD2 system is fitted. |  |  | 11
24 | [6 empty] | 11
25 | Is further automatic detection and/or manual alarm provision required? If yes, state what. | No |  |  |  |  | 11
25 | [6 empty] | 11
26 | Is the fire alarm system in working order? | n/k | P3 | Unable to ascertain if flats have smoke detection and if in working order. |  |  | 12
26 | [6 empty] | 12
Limiting fire spread | [6 empty] | 12
27 | Is the level of compartmentation adequate? (Special consideration should be given to converted or non 'purpose built' premises.) | n/k | P3 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate. In addition, all service ducts on the ceilings from all flats require further investigation to confirm compartmentation levels. |  |  | 13
27 | [6 empty] | 13
27 | [6 empty] | 13
27 | [6 empty] | 13
27 | [6 empty] | 13
28 | Are linings appropriate to limit fire spread? | n/k | P1 | Confirmation required that paint is Class 0. If not then provide a class 0 system for all communal parts. |  |  | 14
|  | No | P1+ | There is paint delamination on the ceilings in this block this should be removed and the ceilings redecorated with a flame retardant coating to prevent flashover from occurring.
28 |  | Yes |  | (Reviewed by Paul Williams G.I.F.ire.E, M.I.F.S.M, M.I.I.R.S.M 12-11-2019)We are in receipt of BB7's "Fire safety review of external wall systems" document and the BBA certificate for the external clading and both suggest that the system would meet the requirements of building regulations at the time of construction. We have also taken into consideration the overal risk of the block and can confirm that the Principles of Prevention (Article 10 of the RRFSO) would not be applicable as the life risk is not adversely effected. |  |  | 14
29 | Where required, are dampers provided? | n/a |  |  |  |  | 14
29 | [6 empty] | 14
Fire fighting equipment | [6 empty] | 14
30 | Provision, accessibility and condition of portable fire extinguishers | No |  | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. |  |  | 14
30 | [6 empty] | 14
31 | Provision and condition of other fire extinguishing systems | n/a |  |  |  |  | 14
31 | [6 empty] | 14
32 | Are dry/wet risers in good order? | Yes |  | Last test date: 12/2018. |  |  | 14
32 | [6 empty] | 14
33 | Is fireman's switch working correctly? | Yes |  |  |  |  | 14
33 | [6 empty] | 14
Other issues | [6 empty] | 14
34 | Roof void? | Yes | P3 | It is recommended that a roof void survey is carried out. |  |  | 15
35 | Other (specify) | [5 empty] | 15
36 | [6 empty] | 15
37 | [6 empty] | 15

## M-M
Priority | Description | Timescale |  |  |  | UPRN | B95A1
P0 | When an unacceptable risk to fire safety is present. Note: Works typically carried out by Housing/Repairs | Within 10 days | [6 empty] | Yes | Direct Labour
P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the Note: RESPONSIVE REPAIRS TEAM | Within 6 months | [6 empty] | No | M & E
P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note: PLANNED WORKS TEAM DELIVERY | Within 1 year | [6 empty] | n/k | TSO & ESO
P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years | [6 empty] | n/a | H & S
P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note: PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years | [7 empty] | Asbestos Team
P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural | [7 empty] | FRA Team
Management and maintenance
Premises: | Marsh Drive 73-96, NW9 7QQ (B95 |  |  | FRA date: | 2019-06-26
Question | Management/maintenance | Yes/No n/k - n/a | Priority | Location and comment
Premises management | [6 empty] | 15
38 | Is there a suitable record of fire safety arrangements available? | n/k |  | Records are held centrally by the Health and Safety Team |  |  | 15
38 | [6 empty] | 15
39 | Are appropriate fire safety procedures in place? Consider: Emergency action plans; calling/meeting the fire service; ensuring the premises are evacuated; assembly points; assistance for disabled; information to external contractors; nominated staff duties | No | P1 | There is no evidence of communication to the resident of what to do in the event of fire. We would suggest informing residents to "Stay Safe" in the event of fire and leave if they feel endangered by a fire. |  |  | 16
39 | [6 empty] | 16
40 | Has any liaison taken place with the local fire and rescue service? | Yes |  | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. |  |  | 16
40 | [6 empty] | 16
Training | [6 empty] | 16
41 | Do staff receive induction and/or annual fire safety refresher training? | Yes |  | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. |  |  | 16
41 | [6 empty] | 16
42 | If drills are considered appropriate, are they carried out at regular intervals? | n/a |  |  |  |  | 16
42 | [6 empty] | 16
Maintenance checks | [6 empty] | 16
43 | Are the premises generally well maintained? | Yes |  | The building appears to be generally well maintained with some minor defects that form part of the action plan |  |  | 16
43 | [6 empty] | 16
44 | Do appropriate regular checks take place? | Yes |  | Regular checks of the premises are carried out and any defects reported to the building maintenance office. |  |  | 16
44 | [6 empty] | 16
45 | Is the alarm system adequately maintained? | n/a |  | There is no communal fire alarm. |  |  | 16
45 | [6 empty] | 16
46 | Is the escape lighting adequately maintained? | Yes |  | Last test date: 25/4/19. |  |  | 16
46 | [6 empty] | 16
47 | Are fire extinguishers adequately maintained? | n/a |  |  |  |  | 16
47 | [6 empty] | 16
48 | Are rising mains adequately maintained? | Yes |  | Last test date: 12/2018. |  |  | 16
48 | [6 empty] | 16
49 | Are fireman lifts adequately maintained? | n/a |  |  |  |  | 16
49 | [6 empty] | 16
50 | Is the sprinkler system adequately maintained? | n/a |  |  |  |  | 16
50 | [6 empty] | 16
51 | Is the lightning protection system adequately maintained? | n/k |  |  |  |  | 16
51 | [6 empty] | 16
Records | [6 empty] | 16
52 | Are fire safety maintenance records available for the premises? | Yes |  |  |  |  | 16
52 | [6 empty] | 16
53 | Are fire drills recorded? | n/a |  |  |  |  | 16
53 | [6 empty] | 16
54 | Is fire safety training recorded? | n/a |  |  |  |  | 16
54 | [6 empty] | 16
55 | Are fire alarm tests recorded? | n/a |  |  |  |  | 16
55 | [6 empty] | 16
56 | Are emergency escape lighting tests recorded? | Yes |  | See item 46. |  |  | 16
56 | [6 empty] | 16
Other issues | [7 empty] | 16
57 | [6 empty] | 16
58 | [6 empty] | 16
59 | [6 empty] | 16
60 | [6 empty] | 16
61 | [6 empty] | 16
62 | [6 empty] | 16

## ActionPlan
| Priority | Description | Timescale |  |  | UPRN |  | No
| P0 | When an unacceptable risk to fire safety is present. Works typically carried out by Housing/Repairs) | Within 10 days |  |  | B95A1 |  | n/a
| P1 | These items are regarded as important but a lead-time to organise is recognised to be necessary. Note - Low number of action items per block typically carried out by the RESPONSIVE REPAIRS TEAM | Within 6 months
| P1+ | These items are regarded as important but a lead in time to organise is recognised to be necessary. Note - PLANNED WORKS TEAM DELIVERY | Within 1 year
| P2 | Where an immediate risk to fire safety is not present but improvements/actions are necessary to maintain the essential systems and standards. Note - PLANNED WORKS TEAM DELIVERY | Within 2 years
| P3 | Works to be considered in future improvements or placed onto a future works programme/rolling maintenance programmes. Note - PLANNED WORKS TEAM DELIVERY | To be placed onto a Planned Improvement programme within 3 months of being identified, and works completed within 5 years.
| P4 | Relates to continuing managerial responsibility or recognised best practice guidance. | Management/procedural
FIRE RISK ASSESSMENT ACTION PLAN
| Premises: | Marsh Drive 73-96, NW9 7QQ (B95 |  |  |  | FRA date: | 2019-06-26
| Question | Action to be taken | Priority | Details | Ongoing from last FRA
1 | 4 | Although there is a secure entry system fitted to this block, the Main Entrance Doors and Landing Entrance Door lockes are broken. These should be repaired/replaced. | P1+
2 | 5 | Refuse bins are too close to the means of escape and need to be relocated in a secure area away from the building. | P1
3 | 14 | There are holes in the ceiling of the electrical intake cupboard and these should be fire stopped by a third party accredited company. | P3
4 | 14 | Flat 74 is not an FD30S door and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. | P3
5 | 14 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. | P3
6 | 14 | All Flat Entry Doors are not FD30S doors and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. | P3
7 | 16 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. | P3
8 | 19 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of +30) particularly as this staircase is the main means of escape in the event of fire. | P3
9 | 20 | In the event of a fire high level lighting is obscured to the point of no longer being visible thus leaving the area below the smoke layer in darkness (refer to Clause 6.4 of BS5266-1). Therefore, a suitable escape route lighting system should be fitted at low level to ensure that occupants can see for their means of escape in accordance with Article 14(2)(h) the RRFSO which requires an escape route to be provided with illumination of an adequate intensity. The system should be either powered or photoluminescent and fitted to and BS ISO16069:2017 Clause 6 for electrically powered and Clause 7 for photoluminescent systems. Refer to CIBSE Guide E Fire Safety Engineering Guide paragraph 7.8.4. which states systems can be "powered or photoluminescent." | P3
10 | 22 | No Fire Action Notice is displayed. Display Fire Action Notices in prominent positions throughout the premises. | P1
11 | 24 | In accordance with Article 13 of the RRFSO it is deemed that adequate protection is provided if the flats have an LD2 system (this would include all bedrooms), therefore recommend LD2 system is fitted. | P3
12 | 26 | Unable to ascertain if flats have smoke detection and if in working order. | P3
13 | 27 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate. In addition, all service ducts on the ceilings from all flats require further investigation to confirm compartmentation levels. | P3
14 | 28 | Confirmation required that paint is Class 0. If not then provide a class 0 system for all communal parts. | P1
15 | 34 | It is recommended that a roof void survey is carried out. | P3
16 | 39 | There is no evidence of communication to the resident of what to do in the event of fire. We would suggest informing residents to "Stay Safe" in the event of fire and leave if they feel endangered by a fire. | P1
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63

## Data (hidden)
KeyID | Question | Priority | Location and comment | Ownership | Details | Ongoing from last FRA
0 | 1 | 0 | 0 | #REF! | 0 | 0
0 | 1 | 0 | 0 | #REF! | 0 | 0
0 | 2 | 0 | None noted at the time of survey. | #REF! | 0 | 0
0 | 2 | 0 | 0 | #REF! | 0 | 0
0 | 3 | 0 | 0 | #REF! | 0 | 0
0 | 0 | 0 | 0 | #REF! | 0 | 0
1 | 4 | P1+ | Although there is a secure entry system fitted to this block, the Main Entrance Doors and Landing Entrance Door lockes are broken. These should be repaired/replaced. | #REF! | 0 | 0
1 | 4 | 0 | 0 | #REF! | 0 | 0
2 | 5 | P1 | Refuse bins are too close to the means of escape and need to be relocated in a secure area away from the building. | #REF! | 0 | 0
2 | 5 | 0 | 0 | #REF! | 0 | 0
2 | 6 | 0 | No evidence of fire loads near premises. | #REF! | 0 | 0
2 | 6 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 7 | 0 | 0 | #REF! | 0 | 0
2 | 7 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 8 | 0 | Loft hatch is secured with FB14. | #REF! | 0 | 0
2 | 8 | 0 | 0 | #REF! | 0 | 0
2 | 0 | 0 | 0 | #REF! | 0 | 0
2 | 9 | 0 | The escape stair is satisfactory for the number of persons expected in the building at any given time | #REF! | 0 | 0
2 | 9 | 0 | 0 | #REF! | 0 | 0
2 | 10 | 0 | 0 | #REF! | 0 | 0
2 | 10 | 0 | 0 | #REF! | 0 | 0
2 | 11 | 0 | The number of fire exits are adequate for the number of persons expected to be in the building as per the tables in Approved Document B Building Regulations. | #REF! | 0 | 0
2 | 11 | 0 | 0 | #REF! | 0 | 0
2 | 12 | 0 | 0 | #REF! | 0 | 0
2 | 12 | 0 | 0 | #REF! | 0 | 0
2 | 13 | 0 | The travel distances are satisfactory and in line with the requirements of the Building Regulations, Approved Document B. | #REF! | 0 | 0
2 | 13 | 0 | 0 | #REF! | 0 | 0
3 | 14 | P3 | There are holes in the ceiling of the electrical intake cupboard and these should be fire stopped by a third party accredited company. | #REF! | 0 | 0
3 | 14 | 0 | 0 | #REF! | 0 | 0
3 | 14 | 0 | 0 | #REF! | 0 | 0
3 | 14 | 0 | 0 | #REF! | 0 | 0
3 | 14 | 0 | 0 | #REF! | 0 | 0
4 | 14 | P3 | Flat 74 is not an FD30S door and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. | #REF! | 0 | 0
4 | 14 | 0 | 0 | #REF! | 0 | 0
5 | 14 | P3 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. | #REF! | 0 | 0
6 | 14 | P3 | All Flat Entry Doors are not FD30S doors and should be replaced with certified FD30S doorset by a UKAS accredited door manufacturer which should be fitted in accordance by a third party accredited fire door installer to BS8214 that should be provided with a valid installation certificate. | #REF! | 0 | 0
6 | 14 | 0 | 0 | #REF! | 0 | 0
6 | 15 | 0 | 0 | #REF! | 0 | 0
6 | 15 | 0 | 0 | #REF! | 0 | 0
7 | 16 | P3 | Flats 73-80, the flat windows and vents are not fire rated or insulated up to 1.1m from deck level, it is a requirement to protect the escape route from fire and therefore the height of the fire rated and insulated materials must be raised to 1.1 metres from the deck level. | #REF! | 0 | 0
7 | 16 | 0 | 0 | #REF! | 0 | 0
7 | 17 | 0 | 0 | #REF! | 0 | 0
7 | 17 | 0 | 0 | #REF! | 0 | 0
7 | 18 | 0 | 0 | #REF! | 0 | 0
7 | 18 | 0 | 0 | #REF! | 0 | 0
8 | 19 | P3 | All stair nosings should be easily identifiable to visually impaired and blind persons as a matter of duty of care and should achieve the Light Reflectance Values as set out in ADM (a LRV of +30) particularly as this staircase is the main means of escape in the event of fire. | #REF! | 0 | 0
8 | 19 | 0 | 0 | #REF! | 0 | 0
8 | 0 | 0 | 0 | #REF! | 0 | 0
9 | 20 | P3 | In the event of a fire high level lighting is obscured to the point of no longer being visible thus leaving the area below the smoke layer in darkness (refer to Clause 6.4 of BS5266-1). Therefore, a suitable escape route lighting system should be fitted at low level to ensure that occupants can see for their means of escape in accordance with Article 14(2)(h) the RRFSO which requires an escape route to be provided with illumination of an adequate intensity. The system should be either powered or photoluminescent and fitted to and BS ISO16069:2017 Clause 6 for electrically powered and Clause 7 for photoluminescent systems. Refer to CIBSE Guide E Fire Safety Engineering Guide paragraph 7.8.4. which states systems can be "powered or photoluminescent." | #REF! | 0 | 0
9 | 20 | 0 | 0 | #REF! | 0 | 0
9 | 21 | 0 | The emergency lights appear to be in good order, last test date 25/04/19. | #REF! | 0 | 0
9 | 21 | 0 | 0 | #REF! | 0 | 0
9 | 0 | 0 | 0 | #REF! | 0 | 0
10 | 22 | P1 | No Fire Action Notice is displayed. Display Fire Action Notices in prominent positions throughout the premises. | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 22 | 0 | 0 | #REF! | 0 | 0
10 | 23 | 0 | Where fitted. | #REF! | 0 | 0
10 | 23 | 0 | 0 | #REF! | 0 | 0
10 | 0 | 0 | 0 | #REF! | 0 | 0
11 | 24 | P3 | In accordance with Article 13 of the RRFSO it is deemed that adequate protection is provided if the flats have an LD2 system (this would include all bedrooms), therefore recommend LD2 system is fitted. | #REF! | 0 | 0
11 | 24 | 0 | 0 | #REF! | 0 | 0
11 | 25 | 0 | 0 | #REF! | 0 | 0
11 | 25 | 0 | 0 | #REF! | 0 | 0
12 | 26 | P3 | Unable to ascertain if flats have smoke detection and if in working order. | #REF! | 0 | 0
12 | 26 | 0 | 0 | #REF! | 0 | 0
12 | 0 | 0 | 0 | #REF! | 0 | 0
13 | 27 | P3 | The building has internal stacks and therefore we would recommend that a sample survey of 2 or more flats is carried out to ensure that the compartmentation levels between flats is adequate. In addition, all service ducts on the ceilings from all flats require further investigation to confirm compartmentation levels. | #REF! | 0 | 0
13 | 27 | 0 | 0 | #REF! | 0 | 0
13 | 27 | 0 | 0 | #REF! | 0 | 0
13 | 27 | 0 | 0 | #REF! | 0 | 0
13 | 27 | 0 | 0 | #REF! | 0 | 0
14 | 28 | P1 | Confirmation required that paint is Class 0. If not then provide a class 0 system for all communal parts. | #REF! | 0 | 0
14 | 28 | 0 | (Reviewed by Paul Williams G.I.F.ire.E, M.I.F.S.M, M.I.I.R.S.M 12-11-2019)We are in receipt of BB7's "Fire safety review of external wall systems" document and the BBA certificate for the external clading and both suggest that the system would meet the requirements of building regulations at the time of construction. We have also taken into consideration the overal risk of the block and can confirm that the Principles of Prevention (Article 10 of the RRFSO) would not be applicable as the life risk is not adversely effected. | #REF! | 0 | 0
14 | 29 | 0 | 0 | #REF! | 0 | 0
14 | 29 | 0 | 0 | #REF! | 0 | 0
14 | 0 | 0 | 0 | #REF! | 0 | 0
14 | 30 | 0 | The communal areas should be sterile areas and as such it is considered that fire extinguishers are not required. It should be noted that fire extinguishers can pose a risk to life if used by untrained people. | #REF! | 0 | 0
14 | 30 | 0 | 0 | #REF! | 0 | 0
14 | 31 | 0 | 0 | #REF! | 0 | 0
14 | 31 | 0 | 0 | #REF! | 0 | 0
14 | 32 | 0 | Last test date: 12/2018. | #REF! | 0 | 0
14 | 32 | 0 | 0 | #REF! | 0 | 0
14 | 33 | 0 | 0 | #REF! | 0 | 0
14 | 33 | 0 | 0 | #REF! | 0 | 0
14 | 0 | 0 | 0 | #REF! | 0 | 0
15 | 34 | P3 | It is recommended that a roof void survey is carried out. | #REF! | 0 | 0
15 | 35 | 0 | 0 | #REF! | 0 | 0
15 | 36 | 0 | 0 | #REF! | 0 | 0
15 | 37 | 0 | 0 | #REF! | 0 | 0
15 | 38 | 0 | Records are held centrally by the Health and Safety Team | #REF! | 0 | 0
15 | 38 | 0 | 0 | #REF! | 0 | 0
16 | 39 | P1 | There is no evidence of communication to the resident of what to do in the event of fire. We would suggest informing residents to "Stay Safe" in the event of fire and leave if they feel endangered by a fire. | #REF! | 0 | 0
16 | 39 | 0 | 0 | #REF! | 0 | 0
16 | 40 | 0 | Barnet Homes take a proactive approach to fire risk assessment and liaise with the local fire authority on best practice. | #REF! | 0 | 0
16 | 40 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | #REF! | 0 | 0
16 | 41 | 0 | Staff are given initial fire safety training on induction into the organisation and periodic training thereafter. Training records are held centrally within the HR Department. | #REF! | 0 | 0
16 | 41 | 0 | 0 | #REF! | 0 | 0
16 | 42 | 0 | 0 | #REF! | 0 | 0
16 | 42 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | #REF! | 0 | 0
16 | 43 | 0 | The building appears to be generally well maintained with some minor defects that form part of the action plan | #REF! | 0 | 0
16 | 43 | 0 | 0 | #REF! | 0 | 0
16 | 44 | 0 | Regular checks of the premises are carried out and any defects reported to the building maintenance office. | #REF! | 0 | 0
16 | 44 | 0 | 0 | #REF! | 0 | 0
16 | 45 | 0 | There is no communal fire alarm. | #REF! | 0 | 0
16 | 45 | 0 | 0 | #REF! | 0 | 0
16 | 46 | 0 | Last test date: 25/4/19. | #REF! | 0 | 0
16 | 46 | 0 | 0 | #REF! | 0 | 0
16 | 47 | 0 | 0 | #REF! | 0 | 0
16 | 47 | 0 | 0 | #REF! | 0 | 0
16 | 48 | 0 | Last test date: 12/2018. | #REF! | 0 | 0
16 | 48 | 0 | 0 | #REF! | 0 | 0
16 | 49 | 0 | 0 | #REF! | 0 | 0
16 | 49 | 0 | 0 | #REF! | 0 | 0
16 | 50 | 0 | 0 | #REF! | 0 | 0
16 | 50 | 0 | 0 | #REF! | 0 | 0
16 | 51 | 0 | 0 | #REF! | 0 | 0
16 | 51 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | #REF! | 0 | 0
16 | 52 | 0 | 0 | #REF! | 0 | 0
16 | 52 | 0 | 0 | #REF! | 0 | 0
16 | 53 | 0 | 0 | #REF! | 0 | 0
16 | 53 | 0 | 0 | #REF! | 0 | 0
16 | 54 | 0 | 0 | #REF! | 0 | 0
16 | 54 | 0 | 0 | #REF! | 0 | 0
16 | 55 | 0 | 0 | #REF! | 0 | 0
16 | 55 | 0 | 0 | #REF! | 0 | 0
16 | 56 | 0 | See item 46. | #REF! | 0 | 0
16 | 56 | 0 | 0 | #REF! | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0
16 | 57 | 0 | 0 | #REF! | 0 | 0
16 | 58 | 0 | 0 | #REF! | 0 | 0
16 | 59 | 0 | 0 | #REF! | 0 | 0
16 | 60 | 0 | 0 | #REF! | 0 | 0
16 | 61 | 0 | 0 | #REF! | 0 | 0
16 | 62 | 0 | 0 | #REF! | 0 | 0